## Introduction
DTI Centre for Distributed Generation and Sustainable Electrical Energy
United Kingdom Generic Distribution System (UKGDS) Phase One
UKGDS Generic HV Underground Network
Last updated:
2005-11-29
Introduction
This spreadsheet specifies a UKGDS Phase One generic High Voltage network in the UKGDS standard format.
This is the HV Underground network (HV UG).
Cells in red show data entered directly and represents the UKGDS standard format data for the generic network
Cells in blue are functions of other cells
Cells in black are notes or fixed values
Description and Summary Analysis
The HV UG model is an 11kV urban network fed from a 33kV supply point.
The high-level characteristics of this model are as follows:
urban area
short circuit length
high customer density
underground construction
radial topology
small overall size
Buses | 400 or 275 kV | 0
| 132 kV | 0
| 66 kV | 0
| 33 kV | 1
| 11 kV | 76
| Other kV | 0
| Total | 77
Loads | Number of loads | 75
| Total P | 24.274
| Total Q | 4.8548
| Average P | 0.32365
| Average Q | 0.064731
Generators | Number of generators | 23
Branches | Number of branches | 75
| Total length | 56.825
| Average length | 0.75767
| Average CR1 | 0.088641
| Average CX1 | 0.050207
| Average Rating CM1 | 7.168
Transformers | Number of transformers | 2
| Average TR1 | 0.04707
| Average TX1 | 0.65409
| Average Rating | 26.4
Shunts | Number of shunts | 0
| Average SHR | #DIV/0!
| Average SHX | #DIV/0!

## Diagram
1
1
1
3
4
4
7
8
1
~
3
~
4
~
~
~
~
7
~
~
~
~
~
8
~
~
~
~
~

## System
Parameter | Symbol | Commentary
System MVA Base | SMB | The system MVA base is the base value for all per unit impedances except for generator impedances
Text Description | STD | A brief textual description will identify the model
System Slack Bus | SSB | The system slack bus must have a generator attached and is used in load flow to balance the system
Profile Time | SPT | The profile time will make reference to the profile data and adjust the load and generator values accordingly
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | Symbol | Value
System MVA Base | SMB | 100
Text Description | STD | UKGDS HV UG
System Slack Bus | SSB | 301
Profile Time | SPT | Average

## Buses
Parameter | Symbol | Commentary
Number | BNU | Each bus is identified by a unique number
Name | BNA | Each bus may also be assigned a name but this is not required and will be manipulated for use in the format of simulation programs.
X Co-ordinate | BXC | DINIS requires X and Y co-ordinates for buses. These co-ordinates will be associated with the bus number when it is referenced by other network components. Here, the co-ordinates are derived using simple functions (so are in blue).
Y Co-ordinate | BYC | See above
Base Voltage | BBV | The base voltage, in kV, of this bus
Bus Type | BTY | This parameter must be consistent with other network components. It indicates the type of the bus within the load flow solution. Buses can be of the normal PQ type, of the PV type if they have a generator attached, or be the slack/reference bus.
Status | BST | Buses may be included in the network data but switched off
Target Voltage Magnitude | BTV | A starting value and target value for voltage magnitude, in per unit. This may be set to 1 in the absence of other data. This value is used both as the starting value for the load flow solution and as the target value for voltage control effected by generators, transformers and switched shunts. Thus, this value may form a part of data for other components when translated into proprietary formats.
Minimum Voltage | BVN | The minimum voltage allowed on this bus, in per unit. Some form of voltage control may be assigned to this bus, e.g. generator reactive power output or transformer tap position will be varied to keep the controlled bus voltage within limits.
Maximum Voltage | BVX | The maximum voltage allowed on this bus, in per unit. See above.
Voltage Angle | BVA | A starting value for voltage angle. This value is probably not required and may be set to 0 in the absence of other data.
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | Number | Name | X Co-ordinate | Y Co-ordinate | Base Voltage | Bus Type | Status | Target Voltage Magnitude | Minimum Voltage | Maximum Voltage | Voltage Angle
Symbol | BNU | BNA | BXC | BYC | BBV | BTY | BST | BTV | BVN | BVX | BVA
Values | 301 | EHV33 | 0 | 0 | 33 | Slack | 1 | 1.02 | 0.97 | 1.03 | 0
| 1100 | HV11 | 10 | 0 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1101 | N0101001 | 20 | 0 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1102 | N0101002 | 30 | 0 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1103 | N0101003 | 30 | 10 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1104 | N0201001 | 20 | 20 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1105 | N0201002 | 30 | 20 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1106 | N0201003 | 30 | 30 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1107 | N0301001 | 20 | 40 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1108 | N0301002 | 30 | 40 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1109 | N0301003 | 30 | 50 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1110 | N0403001 | 20 | 60 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1111 | N0403002 | 30 | 60 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1112 | N0403003 | 40 | 60 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1113 | N0403004 | 30 | 70 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1114 | N0403005 | 40 | 70 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1115 | N0504001 | 20 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1116 | N0504002 | 30 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1117 | N0504003 | 40 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1118 | N0504004 | 50 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1119 | N0504005 | 60 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1120 | N0504006 | 70 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1121 | N0504007 | 80 | 80 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1122 | N0504008 | 30 | 90 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1123 | N0504009 | 50 | 90 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1124 | N0504010 | 60 | 90 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1125 | N0504011 | 80 | 90 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1126 | N0604001 | 20 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1127 | N0604002 | 30 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1128 | N0604003 | 40 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1129 | N0604004 | 50 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1130 | N0604005 | 60 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1131 | N0604006 | 70 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1132 | N0604007 | 80 | 100 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1133 | N0604008 | 30 | 110 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1134 | N0604009 | 50 | 110 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1135 | N0604010 | 60 | 110 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1136 | N0604011 | 80 | 110 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1137 | N0707001 | 20 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1138 | N0707002 | 30 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1139 | N0707003 | 40 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1140 | N0707004 | 50 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1141 | N0707005 | 60 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1142 | N0707006 | 70 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1143 | N0707007 | 80 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1144 | N0707008 | 90 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1145 | N0707009 | 100 | 120 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1146 | N0707010 | 30 | 130 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1147 | N0707011 | 50 | 130 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1148 | N0707012 | 60 | 130 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1149 | N0707013 | 80 | 130 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1150 | N0808001 | 100 | 130 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1151 | N0808002 | 20 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1152 | N0808003 | 30 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1153 | N0808004 | 40 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1154 | N0808005 | 50 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1155 | N0808006 | 60 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1156 | N0808007 | 70 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1157 | N0808008 | 80 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1158 | N0808009 | 90 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1159 | N0808010 | 100 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1160 | N0808011 | 110 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1161 | N0808012 | 120 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1162 | N0808013 | 130 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1163 | N0808014 | 140 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1164 | N0808015 | 150 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1165 | N0808016 | 160 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1166 | N0808017 | 170 | 140 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1167 | N0808018 | 30 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1168 | N0808019 | 50 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1169 | N0808020 | 60 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1170 | N0808021 | 80 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1171 | N0808022 | 100 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1172 | N0808023 | 120 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1173 | N0808024 | 130 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1174 | N0808025 | 150 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0
| 1175 | N0808026 | 170 | 150 | 11 | PQ | 1 | 1 | 0.97 | 1.03 | 0

## Loads
Parameter | Symbol | Commentary
Load Bus Number | LBN | Identifies the bus to which the load is attached
Load ID | LID | A number that identifies individual loads if there is more than one on a single bus. Default to 1 if there is only one load on a bus.
Real Power | LPO | The real power of the load in MW. This is likely to be a nominal value that is adjusted with reference to the profile data.
Reactive Power | LQA | The reactive power of the load in MVAr. This is likely to be a nominal value that is adjusted with reference to the profile data. Power factor can be calculated from the real and reactive power values.
Profile Type | LTY | This specifies which profile should be referenced in adjusting the real and reactive power values.
Status | LST | The load may be switched on and off
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | Load Bus Number | Load ID | Real Power | Reactive Power | Profile Type | Status
Symbol | LBN | LID | LPO | LQA | LTY | LST
Values | 1101 | 1 | 0.392 | 0.0784 | 1 | 1
| 1102 | 1 | 0.392 | 0.0784 | 1 | 1
| 1103 | 1 | 0.116 | 0.0232 | 1 | 1
| 1104 | 1 | 0.392 | 0.0784 | 1 | 1
| 1105 | 1 | 0.392 | 0.0784 | 1 | 1
| 1106 | 1 | 0.116 | 0.0232 | 1 | 1
| 1107 | 1 | 0.392 | 0.0784 | 1 | 1
| 1108 | 1 | 0.392 | 0.0784 | 1 | 1
| 1109 | 1 | 0.116 | 0.0232 | 1 | 1
| 1110 | 1 | 0.394 | 0.0788 | 1 | 1
| 1111 | 1 | 0.394 | 0.0788 | 1 | 1
| 1112 | 1 | 0.396 | 0.0792 | 1 | 1
| 1113 | 1 | 0.1 | 0.02 | 1 | 1
| 1114 | 1 | 0.102 | 0.0204 | 1 | 1
| 1115 | 1 | 0.426 | 0.0852 | 1 | 1
| 1116 | 1 | 0.426 | 0.0852 | 1 | 1
| 1117 | 1 | 0.426 | 0.0852 | 1 | 1
| 1118 | 1 | 0.426 | 0.0852 | 1 | 1
| 1119 | 1 | 0.426 | 0.0852 | 1 | 1
| 1120 | 1 | 0.426 | 0.0852 | 1 | 1
| 1121 | 1 | 0.426 | 0.0852 | 1 | 1
| 1122 | 1 | 0.212 | 0.0424 | 1 | 1
| 1123 | 1 | 0.212 | 0.0424 | 1 | 1
| 1124 | 1 | 0.214 | 0.0428 | 1 | 1
| 1125 | 1 | 0.214 | 0.0428 | 1 | 1
| 1126 | 1 | 0.426 | 0.0852 | 1 | 1
| 1127 | 1 | 0.426 | 0.0852 | 1 | 1
| 1128 | 1 | 0.426 | 0.0852 | 1 | 1
| 1129 | 1 | 0.426 | 0.0852 | 1 | 1
| 1130 | 1 | 0.426 | 0.0852 | 1 | 1
| 1131 | 1 | 0.426 | 0.0852 | 1 | 1
| 1132 | 1 | 0.426 | 0.0852 | 1 | 1
| 1133 | 1 | 0.212 | 0.0424 | 1 | 1
| 1134 | 1 | 0.212 | 0.0424 | 1 | 1
| 1135 | 1 | 0.214 | 0.0428 | 1 | 1
| 1136 | 1 | 0.214 | 0.0428 | 1 | 1
| 1137 | 1 | 0.434 | 0.0868 | 1 | 1
| 1138 | 1 | 0.434 | 0.0868 | 1 | 1
| 1139 | 1 | 0.436 | 0.0872 | 1 | 1
| 1140 | 1 | 0.436 | 0.0872 | 1 | 1
| 1141 | 1 | 0.436 | 0.0872 | 1 | 1
| 1142 | 1 | 0.436 | 0.0872 | 1 | 1
| 1143 | 1 | 0.436 | 0.0872 | 1 | 1
| 1144 | 1 | 0.436 | 0.0872 | 1 | 1
| 1145 | 1 | 0.436 | 0.0872 | 1 | 1
| 1146 | 1 | 0.216 | 0.0432 | 1 | 1
| 1147 | 1 | 0.218 | 0.0436 | 1 | 1
| 1148 | 1 | 0.218 | 0.0436 | 1 | 1
| 1149 | 1 | 0.218 | 0.0436 | 1 | 1
| 1150 | 1 | 0.218 | 0.0436 | 1 | 1
| 1151 | 1 | 0.342 | 0.0684 | 1 | 1
| 1152 | 1 | 0.342 | 0.0684 | 1 | 1
| 1153 | 1 | 0.344 | 0.0688 | 1 | 1
| 1154 | 1 | 0.344 | 0.0688 | 1 | 1
| 1155 | 1 | 0.344 | 0.0688 | 1 | 1
| 1156 | 1 | 0.344 | 0.0688 | 1 | 1
| 1157 | 1 | 0.344 | 0.0688 | 1 | 1
| 1158 | 1 | 0.344 | 0.0688 | 1 | 1
| 1159 | 1 | 0.344 | 0.0688 | 1 | 1
| 1160 | 1 | 0.344 | 0.0688 | 1 | 1
| 1161 | 1 | 0.344 | 0.0688 | 1 | 1
| 1162 | 1 | 0.344 | 0.0688 | 1 | 1
| 1163 | 1 | 0.344 | 0.0688 | 1 | 1
| 1164 | 1 | 0.344 | 0.0688 | 1 | 1
| 1165 | 1 | 0.344 | 0.0688 | 1 | 1
| 1166 | 1 | 0.344 | 0.0688 | 1 | 1
| 1167 | 1 | 0.222 | 0.0444 | 1 | 1
| 1168 | 1 | 0.222 | 0.0444 | 1 | 1
| 1169 | 1 | 0.224 | 0.0448 | 1 | 1
| 1170 | 1 | 0.224 | 0.0448 | 1 | 1
| 1171 | 1 | 0.224 | 0.0448 | 1 | 1
| 1172 | 1 | 0.224 | 0.0448 | 1 | 1
| 1173 | 1 | 0.224 | 0.0448 | 1 | 1
| 1174 | 1 | 0.224 | 0.0448 | 1 | 1
| 1175 | 1 | 0.224 | 0.0448 | 1 | 1

## Generators
Parameter | Symbol | Commentary
Bus Number | GBN | Identifies the bus to which the generator is attached.
Generator ID | GID | A number that identifies individual generators if there is more than one on a single bus. Default to 1 if there is only one generator on the bus.
Real Power | GPO | The real power output of the generator in MW. This will remain fixed in a load flow solution unless the generator is connected to the system slack bus. It may be adjusted with reference to a profile.
Maximum Real Power | GPX | The maximum limit of real power, in MW, used for assessing out-of-limit operation. A generator at the slack bus may go out of limits to solve the load flow.
Minimum Real Power | GPN | The minimum limit of real power, in MW. See above.
Reactive Power | GQA | The reactive power output of the generator, in MVAr. This will be varied in a load flow solution according to the voltage control objectives. It may also be adjusted with reference to a profile.
Maximum Reactive Power | GQX | The maximum reactive power output of the generator, in MVAr. A generator with voltage control objectives will vary reactive power within its limits. If generator reactive power is to remain fixed (PQ-type operation) then this value should be set equal to the Reactive Power value. This value becomes part of the busbar data in IPSA. Maximum apparent power can be derived from the limits for real and reactive power.
Minimum Reactive Power | GQN | The minimum reactive power output of the generator, or the maximum reactive power absorbed by the generator, in MVAr. See above.
Profile Type | GTY | This specifies which profile should be referenced in adjusting the real and reactive power values.
Status | GST | The generator may be switched on or off.
Controlled Bus | GCB | The bus where the voltage is being controlled by changes in generator reactive power. Zero indicates that the controlled bus is the bus the generator is connected to. A negative number indicates that no bus is being controlled. Reference is made to the relevant bus data to determine the target, minimum and maximum voltage values. It is recommended that a bus be assigned no more than one generator to control its voltage. This value becomes part of the busbar data in IPSA. In DINIS, the controlled bus is set to the bus to which the generator is attached.
Generator MVA Base | GMB | The MVA base value from which the per unit impedance values for the generator are determined.
Positive and Negative Sequence Resistance | GR1 | The positive and negative sequence resistances of the generator are given the same value. This should be expressed in per unit on generator MVA base.
Positive and Negative Sequence Reactance | GX1 | The positive and negative sequence reactances of the generator are given the same value. This should be expressed in per unit on generator MVA base. This value should be set equal to the direct axis sub-transient reactance of the generator.
Zero Sequence Resistance | GR0 | The zero sequence resistance of the generator. This should be expressed in per unit on generator MVA base. This should incorporate any earthing resistance. Values of zero for zero sequence resistance and reactance indicate that the generator is not earthed.
Zero Sequence Reactance | GX0 | The zero sequence reactance of the generator. This should be expressed in per unit on generator MVA base. This should incorporate any earthing reactance. Values of zero for zero sequence resistance and reactance indicate that the generator is not earthed.
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | Bus Number | Generator ID | Real Power | Maximum Real Power | Minimum Real Power | Reactive Power | Maximum Reactive Power | Minimum Reactive Power | Profile Type | Status | Controlled Bus | Generator MVA Base | Positive and Negative Sequence Resistance | Positive and Negative Sequence Reactance | Zero Sequence Resistance | Zero Sequence Reactance
Symbol | GBN | GID | GPO | GPX | GPN | GQA | GQX | GQN | GTY | GST | GCB | GMB | GR1 | GX1 | GR0 | GX0
Values | 301 | 1 | 30 | 60 | -60 | 10 | 60 | -60 | 1 | 1 | 0 | 100 | 0 | 0.05 | 0 | 0
| 1102 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1105 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1108 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1112 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1116 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1118 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1119 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1121 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1127 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1129 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1130 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1132 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1138 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1140 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1141 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1143 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1145 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1152 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1155 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1159 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1162 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0
| 1166 | 1 | 1.73 | 2.3 | 0 | 0.81 | 1.1 | 0.4 | 1 | 0 | 0 | 2.3 | 0.005 | 0.2 | 0 | 0

## Branches
Parameter | Symbol | Commentary
From Bus | CFB | Identifies the bus at the "from" end of the branch.
To Bus | CTB | Identifies the bus at the "to" end of the branch.
Branch ID | CID | A number that identifies individual branches if there is more than one connected between the same two buses. Default to 1 if there is only one branch between these two buses.
Positive and Negative Sequence Resistance | CR1 | The positive and negative sequence resistances of the branch should be the same value. This should be expressed in per unit on system base.
Positive and Negative Sequence Reactance | CX1 | The positive and negative sequence reactances of the branch should be the same value. This should be expressed in per unit on system base.
Positive and Negative Sequence Susceptance | CB1 | The positive and negative sequence susceptances of the branch should be the same value. This should be expressed in per unit on system base.
Zero Sequence Resistance | CR0 | The zero sequence resistance of the branch. This should be expressed in per unit on system base.
Zero Sequence Reactance | CX0 | The zero sequence reactance of the branch. This should be expressed in per unit on system base.
Zero Sequence Susceptance | CB0 | The zero sequence susceptance of the branch. This should be expressed in per unit on system base.
Rating One | CM1 | Each branch can be assigned three ratings, in MVA. These will be used to assess overloads but may be interpreted in different ways by the three software packages.
Rating Two | CM2 | See above.
Rating Three | CM3 | See above.
Length | CLE | The length of the branch in kilometres. This value is likely to be a tuneable parameter. Changing branch length will have an impact on the branch impedances.
Status | CST | The branch may be switched on (1) or off (0).
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | From Bus | To Bus | Branch ID | Positive and Negative Sequence Resistance | Positive and Negative Sequence Reactance | Positive and Negative Sequence Susceptance | Zero Sequence Resistance | Zero Sequence Reactance | Zero Sequence Susceptance | Rating One | Rating Two | Rating Three | Length | Status
Symbol | CFB | CTB | CID | CR1 | CX1 | CB1 | CR0 | CX0 | CB0 | CM1 | CM2 | CM3 | CLE | CST
Values | 1100 | 1101 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1101 | 1102 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1102 | 1103 | 1 | 0.0624 | 0.017 | 0 | 0.1665 | 0.017 | 0 | 4.84 | 4.84 | 4.84 | 0.236 | 1
| 1100 | 1104 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1104 | 1105 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1105 | 1106 | 1 | 0.0624 | 0.017 | 0 | 0.1665 | 0.017 | 0 | 4.84 | 4.84 | 4.84 | 0.236 | 1
| 1100 | 1107 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1107 | 1108 | 1 | 0.2038 | 0.1056 | 0 | 0.6028 | 0.1014 | 0 | 6.82 | 6.82 | 6.82 | 1.504 | 1
| 1108 | 1109 | 1 | 0.0624 | 0.017 | 0 | 0.1665 | 0.017 | 0 | 4.84 | 4.84 | 4.84 | 0.236 | 1
| 1100 | 1110 | 1 | 0.266 | 0.1378 | 0 | 0.7868 | 0.1323 | 0 | 6.82 | 6.82 | 6.82 | 1.963 | 1
| 1110 | 1111 | 1 | 0.266 | 0.1378 | 0 | 0.7868 | 0.1323 | 0 | 6.82 | 6.82 | 6.82 | 1.963 | 1
| 1111 | 1112 | 1 | 0.266 | 0.1378 | 0 | 0.7868 | 0.1323 | 0 | 6.82 | 6.82 | 6.82 | 1.963 | 1
| 1111 | 1113 | 1 | 0.0663 | 0.018 | 0 | 0.1771 | 0.018 | 0 | 4.84 | 4.84 | 4.84 | 0.251 | 1
| 1112 | 1114 | 1 | 0.0663 | 0.018 | 0 | 0.1771 | 0.018 | 0 | 4.84 | 4.84 | 4.84 | 0.251 | 1
| 1100 | 1115 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1115 | 1116 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1116 | 1117 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1117 | 1118 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1118 | 1119 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1119 | 1120 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1120 | 1121 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1116 | 1122 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1118 | 1123 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1119 | 1124 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1121 | 1125 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1100 | 1126 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1126 | 1127 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1127 | 1128 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1128 | 1129 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1129 | 1130 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1130 | 1131 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1131 | 1132 | 1 | 0.0745 | 0.0574 | 0 | 0.2352 | 0.0582 | 0 | 8.86 | 8.86 | 8.86 | 0.902 | 1
| 1127 | 1133 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1129 | 1134 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1130 | 1135 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1132 | 1136 | 1 | 0.0542 | 0.0147 | 0 | 0.1447 | 0.0147 | 0 | 4.84 | 4.84 | 4.84 | 0.205 | 1
| 1100 | 1137 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1137 | 1138 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1138 | 1139 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1139 | 1140 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1140 | 1141 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1141 | 1142 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1142 | 1143 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1143 | 1144 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1144 | 1145 | 1 | 0.0917 | 0.0706 | 0 | 0.2894 | 0.0716 | 0 | 8.86 | 8.86 | 8.86 | 1.11 | 1
| 1138 | 1146 | 1 | 0.0571 | 0.0155 | 0 | 0.1524 | 0.0155 | 0 | 4.84 | 4.84 | 4.84 | 0.216 | 1
| 1140 | 1147 | 1 | 0.0571 | 0.0155 | 0 | 0.1524 | 0.0155 | 0 | 4.84 | 4.84 | 4.84 | 0.216 | 1
| 1141 | 1148 | 1 | 0.0571 | 0.0155 | 0 | 0.1524 | 0.0155 | 0 | 4.84 | 4.84 | 4.84 | 0.216 | 1
| 1143 | 1149 | 1 | 0.0571 | 0.0155 | 0 | 0.1524 | 0.0155 | 0 | 4.84 | 4.84 | 4.84 | 0.216 | 1
| 1145 | 1150 | 1 | 0.0571 | 0.0155 | 0 | 0.1524 | 0.0155 | 0 | 4.84 | 4.84 | 4.84 | 0.216 | 1
| 1100 | 1151 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1151 | 1152 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1152 | 1153 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1153 | 1154 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1154 | 1155 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1155 | 1156 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1156 | 1157 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1157 | 1158 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1158 | 1159 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1159 | 1160 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1160 | 1161 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1161 | 1162 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1162 | 1163 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1163 | 1164 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1164 | 1165 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1165 | 1166 | 1 | 0.0665 | 0.0512 | 0 | 0.2099 | 0.0519 | 0 | 8.86 | 8.86 | 8.86 | 0.805 | 1
| 1152 | 1167 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1154 | 1168 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1155 | 1169 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1157 | 1170 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1159 | 1171 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1161 | 1172 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1162 | 1173 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1164 | 1174 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1
| 1166 | 1175 | 1 | 0.0729 | 0.0198 | 0 | 0.1948 | 0.0198 | 0 | 4.84 | 4.84 | 4.84 | 0.276 | 1

## Transformers
Parameter | Symbol | Commentary
From Bus | TFB | Identifies the bus at the "from" end of the transformer.
To Bus | TTB | Identifies the bus at the "to" end of the transformer.
Transformer ID | TID | A number that identifies individual transformers if there is more than one connected between the same two buses. Default to 1 if there is only one transformer between these buses.
Positive and Negative Sequence Resistance | TR1 | The positive and negative sequence resistances of the transformer should be the same value. This should be expressed in per unit on system base.
Positive and Negative Sequence Reactance | TX1 | The positive and negative sequence reactances of the transformer should be the same value. This should be expressed in per unit on system base.
Zero Sequence Resistance | TR0 | The zero sequence resistance of the transformer. This should be expressed in per unit on system base.
Zero Sequence Reactance | TX0 | The zero sequence reactance of the transformer. This should be expressed in per unit on system base.
Earthing Resistance | TRE | The earthing resistance of the transformer. This should be expressed in per unit on system base. The role of earthing impedance in fault studies is influenced by the transformed Winding Connection (TWC). See the report on the standard data format for further information.
Earthing Reactance | TXE | The earthing reactance of the transformer. This should be expressed in per unit on system base. The role of earthing impedance in fault studies is influenced by the transformed Winding Connection (TWC). See the report on the standard data format for further information.
Iron Loss | TIL | The no load iron loss in the transformer core, expressed in Watts.
Magnetising Current | TMC | The magnetising current in per unit on system MVA base and nominal primary voltage base.
Rating One | TM1 | Each transformer can be assigned three ratings in MVA. These will be used to assess overloads but may be interpreted in different ways by different software packages.
Rating Two | TM2 | See above
Rating Three | TM3 | See above
Status | TST | The transformer can be switched on (1) and off (0).
Starting Tap Ratio | TTR | The starting point for the transformer tap changer as a per unit nominal ratio. This value can be set to 1 in the absence of other data.
Maximum Tap Position | TTX | The maximum tap position as a per unit nominal value. The max and min tap position can be set equal to the starting ratio to indicate a fixed-tap transformer.
Minimum Tap Position | TTN | The minimum tap position as a per unit nominal value. The max and min tap position can be set equal to the starting ratio to indicate a fixed-tap transformer.
Tap Positions | TTP | The number of tap positions. This should be consistent with the maximum, minimum and starting tap positions.
Winding Connection | TWC | The transformer winding connection: YY, YD, DY or DD. This influences the zero sequence representation of the transformer for fault level studies. This does not influence the transformer phase shift angle (TPS), which must be specified separately. See the report on the standard data format for further information.
Phase Shift Angle | TPS | The transformer phase shift angle in degrees.
Controlled Bus | TCB | The bus where the voltage is being controlled by changes in transformer tap position. Zero indicates that the controlled bus is the "To Bus" of the transformer. A negative number indicates that no bus is being controlled. Reference is made to the relevant bus data to determine the target, minimum and maximum voltage values.
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | From Bus | To Bus | Transformer ID | Positive and Negative Sequence Resistance | Positive and Negative Sequence Reactance | Zero Sequence Resistance | Zero Sequence Reactance | Earthing Resistance | Earthing Reactance | Iron Loss | Magnetising Current | Rating One | Rating Two | Rating Three | Status | Starting Tap Ratio | Maximum Tap Position | Minimum Tap Position | Tap Positions | Winding Connection | Phase Shift Angle | Controlled Bus
Symbol | TFB | TTB | TID | TR1 | TX1 | TR0 | TX0 | TRE | TXE | TIL | TMC | TM1 | TM2 | TM3 | TST | TTR | TTX | TTN | TTP | TWC | TPS | TCB
Values | 301 | 1100 | 1 | 0.04707 | 0.65409 | 0 | 0.55598 | 0 | 0 | 0 | 0 | 26.4 | 26.4 | 26.4 | 1 | 0.97 | 1.03 | 0.85 | 19 | DY11 | -30 | 1100
| 301 | 1100 | 2 | 0.04707 | 0.65409 | 0 | 0.55598 | 0 | 0 | 0 | 0 | 26.4 | 26.4 | 26.4 | 1 | 0.97 | 1.03 | 0.85 | 19 | DY11 | -30 | 1100

## Shunts
Parameter | Symbol | Commentary
Bus Number | SHB | Identifies the bus to which the shunt is connected. Shunt data becomes part of busbar data in PSS/E and part of branch data in IPSA.
Shunt ID | SHI | A number that identifies individual shunts if there is more than one at a single bus. Default to 1 if there is only one shunt at this bus.
Shunt Resistance | SHR | The shunt resistance in per unit on system base. This value should be positive and should reflect the MW value of the shunt at 1 per unit voltage. The resistive and reactive shunt elements are in parallel. Z-shunt in per unit equals S-base divided by the desired S-shunt.
Shunt Reactance | SHX | The shunt reactance in per unit on system base. A positive value indicates a capacitive shunt; a negative value indicates an inductive shunt. This value should reflect the MVAr value of the shunt at 1 per unit voltage. The resistive and reactive shunt elements are in parallel. Z-shunt in per unit equals S-base divided by the desired S-shunt.
Shunt Status | SHS | The shunt can be switched on (1) or off (0).
These rows are hidden for the sake of appearance. Extra blank rows are inserted here so that the data on every sheet begins at row 30.
Parameter | Bus Number | Shunt ID | Shunt Resistance | Shunt Reactance | Shunt Status
Symbol | SHB | SHI | SHR | SHX | SHS
Values